## Load Calc
DG backup Calculation Mezzaria
LOAD CALCULATION | [5 empty] | AS Per Mahagun |  | As per Buyers Association
Sl no | Tower Name | Flat Type | Flat nos | Load/Flat | Total Load | Diversity | Grand Load | Load Factor | Diversity Factor | Peak Grand Load
|  |  |  | (kVA) | (kVA) |  |  |  |  | (kVA)
1 | T1 | 3 BHK | 124 | 10 | 1240 | 0.5 | 620 | 0.7 | 0.986 | 855.848
2 | T2 -Core1 | 3 BHK- Large | 68 | 10 | 680 | 0.5 | 340 | 0.7 | 0.986 | 469.336
3 | T2-Core2 | 3 BHK- Large | 68 | 10 | 680 | 0.5 | 340 | 0.7 | 0.986 | 469.336
4 | T3-Core 1 | 4 BHK-Straight | 68 | 10 | 680 | 0.5 | 340 | 0.7 | 0.986 | 469.336
5 | T3-Core 2 | 4 BHK-Large | 68 | 10 | 680 | 0.5 | 340 | 0.7 | 0.986 | 469.336
6 | T4 | 4 BHK-Staggered | 68 | 15 | 1020 | 0.5 | 510 | 0.7 | 0.986 | 704.004
7 | T5 | 3BHK | 124 | 10 | 1240 | 0.5 | 620 | 0.7 | 0.986 | 855.848
8 | T6 | 3 BHK | 136 | 10 | 1360 | 0.5 | 680 | 0.7 | 0.986 | 938.672
A | Total Flat Load |  |  |  | 7580 |  | 3790 |  |  | 5231.716
B | Common Area Load | [5 empty] | 686 |  |  | 1308
| Grand Total Load in kVA | [5 empty] | 4476 |  |  | 6539.716
[6 empty] | kVA Rating @ 90% DG Loading | 4973.3333 | For PNG fuel | DG loading at 1.79 times | 11706.0916 | Refer sheet 1 for factor 1.79
| DG Selected |  |  |  |  | 2000kVAX02 =1010 kVAX01 no |  |  | DG selected (X) | X=2000 kVAX6 No's
[8 empty] | For Diesel fuel | DG Loading at 1.377 times | 9005.1889 | Refer sheet 1 for factor 1.1.377
[9 empty] | DG selected (Y) | Y=2000kVAX5 Nos
Considering Maint spare
[8 empty] | No of PNG based -DG required=X+1 |  | 2000 kVAX7 nos
[8 empty] | No of Diesel Based DG required=Y+1 |  | 2000kVAX6 Nos

## Common Area
Common Area Load
|  | As per Mahagun |  |  |  |  | As pr Buyers Association
Sl No | Item Description | Unit load | QTY | Total Load | Diversity | Load after Diversity | Unit Load | QTY | Total Load | Load factor | Diversity Factr | Load after factors | Remark
|  |  |  | (kW) |  |  |  |  | (kW)
(A) | Lift
1 | T1 | 17.1 | 3 | 51.3 | 0.5 | 25.65 | 17.1 | 5 | 85.5 | 0.7 | 0.7 | 41.895 | No of lifts given in Mahaguns calculation is not correct
2 | T2 -Core1 | 17.1 | 3 | 51.3 | 0.5 | 25.65 | 17.1 | 4 | 68.4 | 0.7 | 0.7 | 33.516 | Power cons of service lifts not known, as such same rating as normal lift taken
3 | T2-Core2 | 17.1 | 3 | 51.3 | 0.5 | 25.65 | 17.1 | 4 | 68.4 | 0.7 | 0.7 | 33.516 | LF=0.7, DF=0.7 for LIFTs
4 | T3-Core 1 | 17.1 | 3 | 51.3 | 0.5 | 25.65 | 17.1 | 4 | 68.4 | 0.7 | 0.7 | 33.516
5 | T3-Core 2 | 17.1 | 3 | 51.3 | 0.5 | 25.65 | 17.1 | 4 | 68.4 | 0.7 | 0.7 | 33.516
6 | T4 | 17.1 | 3 | 51.3 | 0.5 | 25.65 | 17.1 | 4 | 68.4 | 0.7 | 0.7 | 33.516
7 | T5 | 17.1 | 3 | 51.3 | 0.5 | 25.65 | 17.1 | 5 | 85.5 | 0.7 | 0.7 | 41.895
8 | T6 | 17.1 | 3 | 51.3 | 0.5 | 25.65 | 17.1 | 5 | 85.5 | 0.7 | 0.7 | 41.895
(B) | Club
i | AC | 110 | 1 | 110 | 0.5 | 55 | 110 | 1 | 110 | 1 | 1 | 110 | LF=1, DF=1 for common areas, facilites
ii | Electricals | 55 | 1 | 55 | 0.5 | 27.5 | 55 | 1 | 55 | 1 | 1 | 55
iii | Lift | 10 | 1 | 10 | 0.5 | 5 | 10 | 1 | 10 | 0.7 | 0.7 | 4.9 | LF=0.7, DF=0.7 for LIFTs
( C ) | Common Area Lighting
i | Internal | 60 | 1 | 60 | 0.5 | 30 | 60 | 1 | 60 | 1 | 1 | 60 | LF=1, DF=1 for common areas, facilites
ii | External | 25 | 1 | 25 | 0.5 | 12.5 | 25 | 1 | 25 | 1 | 1 | 25
iii | Basement | 15 | 1 | 15 | 0.5 | 7.5 | 15 | 1 | 15 | 1 | 1 | 15
(D) | Entrance Lobby
1 | T1 | 22 | 1 | 22 | 0.5 | 11 | 22 | 1 | 22 | 1 | 1 | 22 | LF=1, DF=1 for common areas, facilites
2 | T2 -Core1 | 25 | 1 | 25 | 0.5 | 12.5 | 25 | 1 | 25 | 1 | 1 | 25
3 | T2-Core2 | 0 | 1 | 0 | 0.5 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | Understand common lobby for T2 Core 1 & 2
4 | T3-Core 1 | 25 | 1 | 25 | 0.5 | 12.5 | 25 | 1 | 25 | 1 | 1 | 25 | LF=1, DF=1 for common areas, facilites,
5 | T3-Core 2 | 0 | 1 | 0 | 0.5 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | Understand common lobby for T3 Core 1 & 2
6 | T4 | 20 | 1 | 20 | 0.5 | 10 | 20 | 1 | 20 | 1 | 1 | 20 | LF=1, DF=1 for common areas, facilites
7 | T5 | 22 | 1 | 22 | 0.5 | 11 | 22 | 1 | 22 | 1 | 1 | 22
8 | T6 | 22 | 1 | 22 | 0.5 | 11 | 22 | 1 | 22 | 1 | 1 | 22
(E) | Plumbing & Fire Fighting
i | Pump Room
a) | Filter feed Pump | 20 | 1 | 20 | 0.5 | 10 | 20 | 1 | 20 | 1 | 1 | 20 | These are essential service & there has to be standby loads. Connected load not properly shown. Only operating load has been shown , as such load factor =1 and diversity factor=1
b) | Water Transfer Pump | 44 | 1 | 44 | 0.5 | 22 | 44 | 1 | 44 | 1 | 1 | 44
c) | Jockey Pump | 15 | 1 | 15 | 0.5 | 7.5 | 15 | 1 | 15 | 1 | 1 | 15
[10 empty] | 1 | 1 | 0
(F) | STP | [8 empty] | 1 | 1 | 0
a) | STP | 70 | 1 | 70 | 0.5 | 35 | 70 | 1 | 70 | 1 | 1 | 70
c) | Flushing Water Transfer Pump | 44 | 1 | 44 | 0.5 | 22 | 44 | 1 | 44 | 1 | 1 | 44
[10 empty] | 1 | 1 | 0
(G) | Basement Ventilation | 220 | 1 | 220 | 0.5 | 110 | 220 | 1 | 220 | 1 | 1 | 220
|  |  |  | Total Load in kW |  | 617.2 |  |  | Total Load in Kw |  |  | 1112.165
|  |  |  | Total Load in kVA at 0.9 PFW |  | 685.7778 |  |  | Total Load in kVA at 0.85 PF |  |  | 1308.4294

## Cost
COST
Sl No | Item | Unit | Value
1 | Total Backup power of flats | kVA | 7580
2 | Cost collected from buyers Rs per kVA | Rs/kVA | 40000
3 | Total amount collected from buyers for power backup | Rs | 303200000
4 | Approx cost of one 2000 kVA DG Set | Rs | 150000
5 | No of 2000 kVA DG Sets Reqd | No | 6
6 | Total cost of 6 DG Sets of 2000 kVA each | Rs | 900000